## Slide 1: Hitachi NAS5000
Storage Architecture and Best Practices

## Slide 2: Storage Framework
Shares and Exports are assigned to an EVS and each point to a File System Path
Virtual Servers reside on a cluster node and each have one or more file systems.
File System capacity is allocated from a Span (NAS Storage Pool)
Virtual Volumes are quota trees carved from File System Capacity (Shares/Export typically point to ViVols)
Spans are composed of System Drives /DP Volumes that are drawn from an HDP Pool
Multiple EVS
ViVols
File Systems
Storage Pool
Shares
Exports
Storage Pool
File System
Virtual
Volumes
Storage Pool
File System
Virtual
Volumes
Storage Pool
File System
Virtual
Volumes
SD
SD
SD
SD
SD
RG
RG
RG
RG
RG
HDP POOL
DPVOL
DPVOL
DPVOL
DPVOL
DPVOL
LDEV
LDEV
LDEV
LDEV
LDEV
HDP Pools
Notes: Today we will be discussing Hitachi NAS Storage Architecture and Best Practices
The Hitachi NAS 5000 Solution is a NAS Gateway solution that is built on top of Hitachi world class VSP Block Storage, in particular Hitachi’s Wide Striping Thin Provisioning Layer known as HDP Hitachi Dynamic Provisioning.
On to of that layer are Hitachi NAS Spans or Pools that serve as an aggregation layer on top of which the NAS File Systems are created. Within the File Systems are Virtual Volumes, which serve as a storage/security partition within the file system upon which Shares, Export are created.
The File Systems are mounted by Virtual Servers. Virtual Servers reside on the Physical Nodes of the Cluster, up to 64 Virtual Servers may reside on a cluster of up to 8 nodes. This provides an architecture which allows capacity and performance to scale up and scale-out.

## Slide 3: Physical FC Layer
Notes: Let’s examine the Physical FC Layer

## Slide 4: Fibre Channel Configuration
Hitachi NAS 5000 supports 4 FC Ports per Node
  The port can auto-negotiate to 4,8,16GB FC
  N Port support only (NL mode is not supported)
  Ports numbered in R to L 1,2,3,4
Configuration
  fc-fabric (view fabric)
  fc-hports (view host ports)
  fc-link (enabled/disable)
  fc-ports (view all remote target ports)
  fc-nodes (view WW name of target nodes)
Notes: Each Hitachi NAS Server node has 4 integrated Fibre Channel ports to attach to Hitachi Block Storage
The Hitachi NAS Supports N port only – both Fabric and Direct Attach.
The ports are numbered Right to Left 1,2,3,4
A few CLI commands that are useful when working with the FC layer
Fc-fabric is a useful CLI tool that shows the WW node name of the Fibre Channel fabric the server is connected to
Fc-link this command is used to enable or disable a Fibre Channel interface on the server. The settings apply to all nodes in a cluster.
Fc-ports - displays summary or verbose information about all the FC remote ports discovered by the server.
Fc-nodes - List the WW node name of each fibre channel target node that the server has discovered
Fc-hports - Display information about all server host ports

## Slide 5: FC Wiring
Both direct attach and fabric is supported
Direct attach support max 2 storage subsystems. Clusters with more than 2 nodes require a switch
When attached through a switch, both nodes must see the exact same storage ports
Limit SD paths to 16 (2 HNAS host ports per switch x 2 switches x 4 target ports per switch)
Avoid sharing storage ports with other block hosts
Notes: In terms of wiring the NAS System to the Storage
Direct attach and Fabric attach are both supported, although when direct attached a max of 2 storage subsystem are supported. Clusters with more than 2 nodes require a switched back-end also.
To correctly failover between nodes, the HNAS system must see the same view of the storage from both nodes.
When fabric attached, each nodes should be wired such that each node views the same target ports – the view of the storage system should be consistent across all cluster nodes
It is generally best to limit SD paths to 16 – 2 HNAS hports per switch x 2 switches, 4 target ports per switch
It is not necessary to create multiple host storage domains for each HNAS hport on a specific VSP FC port. A single host storage domain is sufficient. Use the standard default host mode.
The storage ports used by HNAS should be dedicated to it and not shared with other block hosts

## Slide 6: FC Wiring Examples
Direct Attached
Switch Attached
*Note HNAS5k ports numbering is reversed
4,3,2,1
Notes: When looking at the Switch Attach, the zoning should be single initiator zoning.
This is an older diagram that show the port numbers left to right. HNAS5000 actually has 1,2,3,4 right to left.
All LUNs available through all ports
Node 1 Port 1 1A, 1B,2A,2B
Node 1 Port 2 1A, 1B,2A,2B
Node 1 Port 3 3A,3B,4A,4B
Node 1 Port 4 3A,3B,4A,4B
Node 2 Port 1 1A,1B,2A,2B
Node 2 Port 2 1A,1B,2A,2B
Node 2 Port 3 3A,3B,4A,4B
Node 2 Port 4 3A,3B,4A,4B

## Slide 7: Load Balancing
You can display information about host and target port load and paths via the CLI
  fc-host-port-load
  fc-target-port-load
  sdpath
The Server attempts to balance SDs path based on the open SD count
  Load on Storage controller target ports takes precedence over balancing FC host ports.
  Load on Storage controllers takes precedence over balancing ports on those controllers.
Notes: If the system is wired correctly, the Hitachi NAS server should automatically balance LUNs across Host Ports and Target ports to provide an even load balance across controllers. This insure that sufficient queue depth is provided for the number of LUNs presented via each storage port.
You can check on the host port and storage port balancing, by running the command fc-host-port-load and fc-target-port-load
If necessary you can set a preferred path using sdpath command, although this shouldn’t be necessary
Note that the load balancing first attempts to balance LUN across storage controller target ports, then across storage controllers, then across host ports.
Avoid presenting LUNs to the server if they are not used, so that the server doesn’t factor these LUNs into the balancer.

## Slide 8: Example
HNAS-5000-DC1-1:$ fc-host-port-load
1: 3 devices
2: 3 devices
3: 3 devices
4: 3 devices
HNAS-5000-DC1-1:$ fc-target-port-load
03/A/5040D327-1: 12 devices
03/A/5040D327-2: 12 devices
HNAS-5000-DC1-1:$
Notes: Ideally, you should see a balance of LUNs across host ports and target ports

## Slide 9: Storage Controller

## Slide 10: Storage Array Specifics
HNAS 5000 exclusively supports Hitachi Storage Subsystems
HUVM (Storage Virtualization) is also supported
  Consult the current UVM matrix for supported storage systems
Use the standard (default) host mode . A single host storage domain is sufficient for all HNAS hports
Always enable HMO 7 and 68 on each storage ports used by HNAS
When using an HNAS 5000 in a stretched cluster with GAD
  Enable HMO 78 on the host group containing the HNAS WWPN for the “remote” system (so that HNAS uses local storage paths)
Notes: HNAS5000 supports all Hitachi Storage
You cannot directly attach 3rd party storage to an HNAS, but you can attach 3rd party storage that is virtualized by HUVM (It has to be supported by HUVM)
Use the standard default host mode for HNAS. A single host storage domain for all HNAS host ports is sufficicent
Hitachi NAS requires HMO7 and 68 Host Mode Option on Enterprise Storage. HMO7 provides an automatic notification of changes to storage. HMO68 is required for HDP Integration to operate correctly so that HNAS can perform unmapping functions.
When using HNAS5000 in a stretched cluster with GAD, HMO78 should be set on the host group of the ports used by the “remote” system. This insures that HNAS uses local paths over remote paths.

## Slide 11: HDP
The use of Hitachi Dynamic Provisioning (HDP) is strongly recommended:
  Improves performance by striping I/O across all available disks
  Supports larger LUs, up to 64 TiB
  Reduces the need to use the span-expand command.
File system creation and expansion are safe, even on thinly provisioned HDP pools, because they check the amount of available space
See HDP Section later in this presentation
Notes: We strongly recommend the use of THINLY provisioned HDP Pools with HNAS
HDP in particular allows performance to scale linearly as capacity is added.
It supports larger LUN size (up to 64TB)
If Thinly provisioned, the pool can be grown incrementally by adding pool volumes to the HDP Pool without having to run span-expand.
HNAS is “Thin friendly”, file system creation and expansion are safe – because they check for space before creation/expansion operations.

## Slide 12: Storage Pool Layer
Notes: Let’s look now at the NAS Storage Pool Layer

## Slide 13: Span (Storage Pools) and System Drives
LU
LU
LU
LU
LU
SD
SD
SD
SD
SD
4M Stripe
Chunks
Storage Pool / Span
HNAS Storage Pool/Span consists of one or more System Drives (SD)
HNAS creates an SD for each LUN that is discovered. System Drives must be allowed access before HNAS can use them.
A Span can be expanded, but not shrunk
Capacity is divided into chunks (1-18GB)
File systems are allocated 1 or more chunks from the span as they expand.
Max 60,000 chunks per pool
Notes: An HNAS Storage Pool is composed of multiple system drives – as few as four and as many as thirty two
Each System drive is a LUN (DP Volume)
You can expand an existing Span, but you can’t shrink one.
Spans are made up of logical units known as “Chunks”. Chunks are units of capacity assigned by the Span to file systems.
The chunk size is defined at span-creation – it could be as little as 1GB and as large as 18GB.
A span or file system can have to up 60,000 chunks.
When a file system is created or expanded, the HNAS will allocated one or more chunks.

## Slide 14: Spans, Stripe Sets and DWB
Creating a span gets you one stripe set
Expanding a span adds a further stripe set
Chunks reside on a stripe set, DWB attempts to balance writes across stripe sets
  Write operations will be directed to every stripe-set on which the FS has free space.
  If a span has >1 stripe-sets and most free space is on a new stripe-set, all writes will direct there
HDP will balance all physical writes
Notes: When a Storage Pool/Span is created, the system creates an initial/first stripe set
If you ever expand the span, then another stripe set is created and added to that span.
The chunks can reside on one strip set. The server uses a mechanism called DWB to balance writes across stripe sets. The HNAS will write to every stripe-set on which the file systems has free space, but if a span has >1 stripe set, it will prefer writing to the stripe set where there is more free space.
This could mean that when a new stripe set is added to an existing pool that is almost full, that most writes will goto the new stripe set and prefer those underlying LUNs/SD.
However if the span is based on HDP, HDPs will insure that all writes are spread across all pages (PGs within the pool), so a dispersal of IO across all spindles still occurs
Internally it may look like certain SDs are being preferred and indeed more queue operations will occur to those SDs.

## Slide 15: The Span Chunk Allocator
An algorithm that manages the expansion of file systems across multiple stripe-sets
Balances four goals
  Attempts to clump together consecutive chunks from the same file system so as to maximize efficiency / scalability and achieve 60,000 chunks per file system
  Attempts to balances total load across stripe sets
  Attempts to spreads each file system across all stripe sets
  Attempt to draws new chunks from as many stripe sets as possible
See the `span-tune-allocator’ man page for more details
Notes: The span-chunk allocator is an internal algorithm that manages the expansion of file systems across multiple stripe set
Historically, spans and file systems were limited to 1,023 chunks. In 11.2 an enhancement was delivered, that expanded this to 60,000 working around some VLSI limitations.
VLSI continues to operate internally with a table entry limit of 1,024, but rather than mapping that directly to chunks, these now becomes “runs” – a run can consists of one or more chunks.
The span-chunk-allocator works with this enhancements to try to allocate consecutive chunks to maximize runs, while still providing flexibility and achieve 60,000 chunks per file systems
It tries to balance the load evenly across all the span's stripesets so that, if all filesystems are evenly loaded, all storage will be equally loaded.
It tries to spread each filesystem evenly across all available stripesets, so that, if only one or two of a span's filesystems are heavily loaded, all storage will still be evenly loaded.
It tries to ensure that new chunk allocations are drawn from as many stripesets as possible. Newly allocated chunks usually receive more write operations than other chunks.

## Slide 16: Tiered File System (TFS)
Hitachi NAS provides a feature known as TFS or “Tiered File System”
When configuring the span, a Stripe Set is created for each tier
  The metadata tier (Tier 0). Smaller capacity, typically SSD based DP Vols
  The data tier (Tier 1). The data payload, SSD/SAS or NL-SAS DP Vols
Both tiers require at least 4 SDs, typically from separate DP Pools
Span
T0 : DP Vols
T1: DP Vols
User Data
Metadata
TFS separates metadata from data at the SD/stripe set layer of the pool
Notes: Tiered File System (TFS) is a feature of Spans. It allows file systems built on top of those spans to separate data from metadata into separate DP volumes (storage devices)
Metadata is typically a much smaller portion of the data (less than 10% of the overall capacity).
A TFS based span will typically use SSD DP Volumes to store metadata, while using SAS or NL-SAS DP Volumes to store data.
Both tiers require at least 4 SDs – usually from separate HDP Pools, although they can be from the same HDT Pool where the SDs used for Tier0 are “pinned” into the Flash layer of the HDT pool.

## Slide 17: Tiered File System (TFS)
All File systems created on a tiered pool inherit metadata tiering
Can be retroactively applied but not undone
Tier 0 and Tier 1 can be expanded independently
  If Tier 0 capacity is exhausted, Tier 1 will be used for metadata, but no more file systems can be created on that pool (until more capacity added to Tier 0)
  If Tier 0 capacity exhausts, performance will be impacted
Amount of metadata capacity required depends on file system density
  fs-analyze-metadata-usage can be used to determine metadata consumption
  Typical consumption is 10%, but can be much lower when storing larger files e.g. Virtual Machines, CommVault Disk Library, VOD Library
Notes: Once a Tiered Pool is created all file system on that pool inherit metadata tiering
It is possible to turn a nonTFS pool into TFS, but not the other way around.
Tier 0 and Tier 1 can be expanded independently and often are.
If Tier 0 exhausts, then metadata overflows into Tier1, although this will impact performance. If this occurs, the system will not allow more file system to be created on the pool until more capacity is added to Tier 0
The amount of metadata capacity require depends on file system density which is driven a lot by average file size.
The average is 10%, but can be higher when dealing with dense file systems with very small files (32k or less) or can be much lower (2%) if storing large file (like VMs, Disk Libraries or Videos)
The HNAS CLI command fs-analyze-metadata-usage can be run against an existing FS to understand it’s metadata consumption.

## Slide 18: HDP Hitachi Dynamic Provisioning
Notes: Let’s talk about HDP briefly

## Slide 19: Hitachi Dynamic Provisioning
All current Hitachi storage supports HDP
From release 12.1, all HNAS servers support HDP without any additional license
HDP support is not limited to a specific subsystem
HDP has no effect on front end protocol interaction (NFS, SMB)
Notes: HDP – Hitachi Dynamic Provisioning is supported by all Hitachi Storage
HNAS Integration with HDP begins at FW level 12.1
There are no specific array requriements
It does not affect the way NFS/SMB operate

## Slide 20: What is HDP?
SD
SD
SD
SD
SD
PG
PG
PG
PG
PG
HDP POOL
DPVOL
DPVOL
DPVOL
DPVOL
DPVOL
HDP is a Virtual RAID layers that provides thin provisioning and wide-striping capabilities
Multiple LDEVs created on top of PGs
HDP Pool created from Multiple LDEVs (Pool Volumes)
Create Virtual LUs, called DP-Volumes, on top of the DP Pool
HNAS sees the DP-Volumes, not the PGs or the LDEVs
Total capacity of DP-Volumes can exceed the physically installed capacity (Thin Provisioning)
Real disk space is allocated from parity groups the first time the server writes to the DP-Volumes
I/O to a single DP-Vol is multiplexed among all pool volumes
LDEV
LDEV
LDEV
LDEV
LDEV
LDEV
LDEV
LDEV
Notes: HDP is a thin-provisioning virtualisation layer in Hitachi storage
An HDP pool is a collection of storage with physical Raid arrays (pool volumes) at the bottom and virtual LUs (DP-Vols) at the top
LDEVs are created from the PGs and placed into an HDP Pool – these LDEVs are known as “Pool Volumes”
Virtual Volumes or DP Volumes are created on top of the DP Pool. DP Volumes can exceed the capacity of the DP Pool – this is THIN provisioning.
Real capacity is allocated from the PGs the first time the server writes to the DP Volumes. Capacity is allocated in 42MB pages.
I/O to a single DP-Vol is multiplexed among all pool volumes – this is wide striping

## Slide 21: What is “Thin Provisioning”?
Total capacity of a pool’s DP-Volumes can exceed that of its pool volumes
  E.g. Pool volumes total 30TB, DP-Volumes total 60TB
  Looks to (most of) the server like 60TB of storage
HDP allocates pages of real disk space as the server writes data
  Each page is 42MB
  Each page resides on a single pool volume
The server can write anywhere on any DP-Volume, but not everywhere
  It can’t exceed the amount of physical capacity provided by the pool volumes
Notes: Thin Provisioning basically means that the HDP Pool’s capacity can exceed that of the allocated pool volumes.
So I may have 30TB of Pool Volumes (real capacity), but I can create 60TB of DP Volumes. This would be a 200% over subscription.
HDP only allocates real capacity as the server writes data and does so in 42MB pages. Each page resides on a single pool volume.
The server can write anywhere on any DP Volume, but it can’t write everywhere – That is to say, that it can’t exceed the physical capacity of the pool. It can only write to the available physical capacity.

## Slide 22: HDP Thin Provisioning with NAS
Notes: Let’s talking about How Thin Provisioning operates with HNAS

## Slide 23: Why Thin Provision?
Improve performance by striping I/O across all available disks
Provides better scalability (max SDs is 512, max SD size is 64TB)
  Using larger SD size therefore allows the cluster to support higher max. capacity
It should minimally reduce if not eliminate the need to run `span-expand’ and reduce concern with multiple stripe sets and how chunks are balanced across stripes etc..
You can incrementally expand an HNAS system (1PG at a time)
  You can easily add capacity to the Span (without having to actually expand it). Add PG, create Pool Vols, add to HDP Pool, HNAS automatically recognizes capacity.
  Performance always improves as you add PGs, because HDP restripes existing data (no need to expand span or file systems to see benefits)
Notes: Why should we thin provision?
Using LUNs from an HDP pool will maximize performance, due to the multiplexed IO/wide stripi
Using larger “thin” LUNs allows better HNAS scalability. Using larger (up to 64TB LUNs) allows HNAS to reach it’s 32PB max scalability, since the max LUNs is 512 per cluster
The main reason though is to provide an ease of incremental expansion.
Prior to HDP, in order to add capacity to a span, the span had to be expanded, but it has to be expanded in equal fashions. For example, if the Span initially had 4 Volumes based on 4 PGs, the expansion needed to have a similar geometry (4 Volumes on 4 PGs) to provide consistent performance across the two stripe sets.
By thin provisioning, we may not even have to expand the span at all. By creating a span based on “THIN” volumes, to add capacity, we just add more pool volumes to the HDP Pool. The HDP Pool automatically rebalances pages across pool volumes thereby eliminating hot spotting and providing scaling performance with additional capaicyt.

## Slide 24: Hitachi NAS is Thin Friendly
When you create or expand a filesystem, NAS allocates one or more “chunks” (typically 18GB)
If the span resides on HDP storage the HNAS will
  Check for available space (in the span)
  If necessary, chooses a stripeset with enough space
  Write one (non zero) block to each 42MB page in the chunks it allocates
This action prompts HDP to map HDP pages
A file system write will never fail for lack of space (space is mapped). HNAS is Thin Friendly.
Pre-allocation takes time, so we limit allocations when using HDP (1TB)
  CLI can be looped (--storage-is-lightly-loaded)
Enabling “filesystem-thin” allows applications to “see” the confined capacity of the file system
Notes: In order to do this, the HNAS was enhanced to be “THIN” friendly.
Whenever a file system is created or expanded, necessitating the need to add chunks, the span layer in HNAS checks for available space in the HDP pool.
It writes one (non zero) block to each 42MB HDP Page required to fulfill the addition of the span chunks to the file system. This prompts HDP to map HDP pages – in other words, it guarantees that the capacity is physically allocated and that file system will never fail due to lack of space – the HNAS know ahead of time – it will not allow file system creation/expansion to take place if there is insufficient capacity.
The up front mapping of capacity, is known as pre-allocation – it requires IO and takes some time – so allocations are limited to 1TB when creating or expanding file systems.
The CLI does provide a means for performing large expansions (using a flag –storage-is-lightly-loaded), but should only be done when required..
Generally speaking it is best to let file systems auto-expand as required – by default a file system will auto-expand at 85% full up to the configured auto-expansion limit.
If an administrator wishes applications to view their auto-expansion capacity rather then the current fs capacity, they can enable file system thin provisioning.. This enable an application to “see” a much larger file system than what is physically allocated, but allows the system to auto-expand as the application writes to the file system and it reaches the auto-expansion threshhold.
Auto-expansion threshhold and rates of expansion can be configured

## Slide 25: Leveraging Thin Provisioning
Create enough DP-Vols to meet the eventual size of the span and provide sufficient queue depth
  Modestly thin-provision (2 or 3:1) to avoid running out of array shared memory
  You can do more (depends on array).. but Max span is 1PB, max SD Size is 64TB, max SDs is 512
Create a span (single stripe set) across the thinly provisioned DP Volumes
  Use filesystem-thin and span/file-system confine to set auto-expansion limits as appropriate
How do I add capacity to a Thin provisioning Span?
  Ensure that the span is confined
  Add PGs (Pool Volumes) which adds real storage (Allow the pool to rebalance). The new pool volumes match the performance of the existing volumes to provide consistent performance.
  The Server will auto-detect the capacity, but can be expedited (span-expedite-hdp-space-check)
  Release the confinement on the span/file-systems to allow them to auto-expand onto the new capacity if required.
Notes: So.. How do we implement a thin provisioned system?
Generally speaking, you want to create enough DP Volumes for that span to meet it’s projected eventual size with enough SDs to provide sufficient queue depth. (more on this later)
Modes thin provisioning of 2 or 3:1 is typical.. Over aggressive thin provisioning (>300% tends to use up a lot of array shared memory)
Create the span based on these DP Volumes (one single stripeset).
Use file system-thin or setup filesystem confinement (auto-expansion) limits as appropriate.
How do I add capacity to this span..
First insure that span is confined
Add PGs/Pool Volumes to the HDP pool. These should be of the same type/geometry as the existing pool volumes/PGs
The HNAS will auto-detect the new capacity.
Release the span and re-set any auto-expansion limits allowing file system to expand again.

## Slide 26: Pool Growth: Example
Storage Pool/Span
Stripe Set
DPvol
In this example, 4 RGs consisting of 4 x 6+2 R6 are configured in an HDP pool. A total of 8 DP Volumes are created, each equal in size with an oversubscription of 2:1.
As PGs are added to the pool, the available performance (IOPS) increases. The SD q-depth can be tuned.
The Span starts at 2:1 oversubscription, but overtime it reaches 1:1 as capacity is added.
After reaching 1:1, in order to add capacity, the span must be expanded
RG
RG
RG
RG
Chunks
File System
SD
SD
SD
SD
SD
SD
SD
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
SD
RG
RG
RG
RG
Notes: This is a simple example showing a 200% oversubscribed span based on a single HDP Pool.
It starts out with 8 SDs based on 4 PGs.
As PGs / Pool Volumes are added to the pool, the real capacity of the span increases allowing file systems to grow/expand.

## Slide 27: How do I expand the Span when it reaches 1:1?
What happens when the total size of the pool volumes reaches the total size of the DP-Vols and the span still needs more space?
  Add pool volumes to the original pool: just as many as you need; typically, only a little extra space
  Add more DP-vols to the same HDP pool: the same size and number as you originally created
    This is where the rule about all stripesets being the same comes into play
  Wait for formatting to finish
    Otherwise, file systems may auto-expand on to the new storage and find it so slow that the entire span fails
  Expand the span on to the new DP-Vols
Notes: After reaching 1:1 - no oversubscription, the span will need to be expanded
Add PGs, a few more pool volumes
Add an identical stripe set to the existing one – if the first stripe set was 8 x 10TB Volumes, the second should also be 8 x 10TB Volumes
This takes us back again to 200% over subscription.
Wait for all the formatting to complete.
Then expand the span onto the additional DP Volumes.

## Slide 28: Span Expansion: Example
Storage Pool/Span
Stripe Set
DPvol
RG
RG
SD
SD
SD
SD
SD
SD
SD
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
SD
RG
RG
Stripe Set
DPvol
SD
SD
SD
SD
SD
SD
SD
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
DPvol
SD
Chunks
File System
RG
RG
RG
RG
RG
RG
RG
RG
RG
RG
RG
RG
Additional thin DP volumes (equal in size to the original volumes) are created within the DP pool and presented to the HNAS.
Span is expanded (by another stripe set)
The addition of the stripeset alters the overall oversubscription back to the 2:1 ratio.
Since the Span now has 2X more SDs, the q-depth may require tuning.
This process can be repeated until the max span capacity reaches 1PB, although a span can only be expanded a maximum of 63 times and has a 60k max chunk limit.
Notes: This illustration shows what occurs when the second strip set is added.
The Span goes from 1 x 8 SDs to 2 x 8 SDs or 2 stripe sets of 8 SDs
This resets the oversubscription back to 200%
The addition of more DP Volumes may require some tuning of q-depth – the CLI command sd-set –q can tune SD queue depth if necessary.
This can be repeated up to 63 times, although you are more likely to reach the 60k chunk limit first.
All in all it is best if we can simply plan for a single thin provisioned stripe set to last the implementation of the storage array/NAS

## Slide 29: Best Practices & Architectural Guidelines
Notes: Let’s go over some of those guidelines and best practices again

## Slide 30: Guidelines and Best Practices
Oversubscribe the HDP pool by 2-3X the initial size (2-3X is an estimate of lifetime growth).
  High Oversubscription Ratio requires more array shared memory (HDP metadata).
The initial span must consist of at least 4 SDs (system won’t allow less than 4)
  We need at least 4 SDs to create parallelism and q depth, but larger stripesets are preferable with larger/high performance configurations
  Maximum SDs per stripe set is 32
Generally best to create a Span Configuration based on 1-2 DP Volumes per HDD based PG. Use Mod 4 configurations (1 SD per port across 4 HNAS ports)
  e.g. A configuration of 6 PGs – 8 DP Volumes. 1 Span, 8 System Drives
SSD/FMD based DP Pools perform best with more SD per PG (4 or 8)
  Just remember that all Stripe-Sets will need to be the same size if you expand.
Notes: As mentioned earlier, the preference is to build spans based on 2-3X the physical capacity.. In some case if you believe the pool configuration is static, then there may be no need to thin provision it at all.
The initial span must have a at least 4 SDs, but larger stripesets can help drive performance by creating more q depth and parralelism. The maximum # of SD per stripe set is 32.
You don’t want to have TOO many SDs either.. The limit is 512 per cluster. So you need to strike the right balance..
Too few.. May not drive enough performance, too many may overdrive it or limit scalability (capacity)
Generally speaking we advise 1-2 DP Volumes per HDD based PG. Certainly 2 DP Volumes per 14+2 and 1-2 per 6+2
SSD/flash based DP Pool perform best with 4-8 SD per PG, although there’s no point in creating multiple stripe sets of 32 SD, even if you have many PGs of Flash.
Remember that qdepth can be tuned on per SD basis, using sd-set –q

## Slide 31: The Minimum HDP Pool Requirements
The 4 SD requirement is (partly) designed to enforce a min. amount of disk spindles
  NAS workloads are frequently undersized. Too often sized to capacity rather than performance and lack the ops provided by multiple HDD PGs
  Prior to HDP, the “Best Practice” was to create 1 SD/LUN per physical HDD PG.
  The 4 SD Best Practice was designed to enforce a min of 4 PGs ~32 HDDs (4 x 6+2)
  HDP Virtualizes PGs, but 4 PGs of HDDs is still a “Best Practice” and should be considered the minimum configuration. For 7.2k NL-SAS consider ~48 NL-SAS HDDs
  14+2 PGs are supported. No requirement to use 6+2.
  Also consider RAID configuration (RAID5 vs RAID6 vs RAID1) drive type and workload
  SSD or FMD based pools, have no min drive requirement
    A single 3+1 R5 PG based pool is supported, but will still require 4 SDs (DP Vols)
Notes: Let’s talk about the minimum requirement though.. As sometimes we deal with very small NAS footprints.
The minimum is 4 SDs – this is based on a need to create a minimum viable pool of 4 PGs – of about 24 10k HDDs – 48 7.2k NL-SAS HDDs
All RAID types are supported including 14+2
Consider your RAID options.. Sometimes RAID1 is best for write intensive workloads.
SSD/Flash have no minimum drive requirement. A single 3+1 is supported.. But you always require at least 4 SDs.

## Slide 32: Rules of Span Configuration/Expansion
Minimum of 4 SDs required for an HDP Based Stripeset
When the span is expanded, the following stripeset must have the same # of SD as the initial stripeset.
As a Best practice, each Stripe-Set should have the same SD configuration (number, size) and should be based on the same PG configuration
  Uniform configuration provides a more predictable performance
  It is permitted (but not a BP) to have Stripe-Sets from separate HDP pools, but all SDs within a Stripe-Set must come from the same HDP Pool
A Span cannot be composed of DP Volumes and Plain Old Parity Groups
  A Span must be HDP or non-HDP (all in or all out)
Pool volumes from a PG should belong to one HDP Pool only
Notes: If you do end up having to expand a NAS pool, remember than when using HDP based spans, that the next stripeset must have at least as many SDs as the first.
So if you started with 8 SDs, the second stripeset must also have at least 8 SDs
The best practice is to keep identical stripe sets with a uniform configuration.
You can’t mix and match DP Volumes from different DP Pools in the same stripeset, but the server will allow you to expand a span with DP Volumes from different DP Pools.
i.e. stripe set 0 could come from DP Pool 0, stripe set 1 could come from DP Pool 1. That is supported, but perhaps not the best way to do it.
You obviously can’t mix and match DP Volumes with non DP Volumes in the same span. The span must be all HDP or all plan LDEVs.
Pool Volumes from a PG should belong to only 1 HDP Pool

## Slide 33: Multiple Spans on a single HDP Pool
It is permitted and sometimes beneficial to create multiple NAS Spans on a single HDP pool
  e.g., Single HDP Pool, create 16 DP Volumes – 8 SDs for Span 1, 8 SDs for Span 2
In many cases multiple Spans per HDP Pool is advantageous
  Spans are limited to 32 file systems, if you need more file systems you need more Spans to achieve that… but large SSDs can create massive single PG HDP Pools (hundreds of TBs that often need multiple EVS/file systems)
  1 Span per HDP Pool might create islands of capacity or islands of IOPS
  Creating multiple spans might help avoid queue splits (see later in presentation)
Previous BP was 1 Span per HDP Pool
  Biggest reason was to avoid possibility of unmap. Unmap had a significant performance impact on HUS1x0 Storage. VSP overhead is minimal
  More file systems result in more IO workload (more file systems must be checkpointed). If storage was slow this could create a bottleneck.
Notes: Can you create multiple Span on top of a single HDP Pool? DP Pool with 16 DP Volumes – 8 for Span 1, 8 for Span 2?
Yes, you can. Although the server will warn you about the possible dangers of doing so before allowing it to happen.
Sometimes multiple Span on an HDP Pool is advantageous or required.
A Span is generally limited to 32 file systems, so creating more than 32 files systems required >1 span. This may be the only way to implement something based on a single PG for high density flash e.g. 7+1 of 30TB drives is over 200TB of capacity.
Having 1 span per HDP Pool could end up creating island of capacity. E.g. If I had 2 PGs for Flash @100TB ea. If I have to dedicate 1 PG for each Span, if 1 span grows faster than the other, then I could end up requiring 130TB on Span 1 and only 30TB on Span 2. If that was all 1 HDP pool, that would be 160TB/200TB… but if that’s split into two, I’m left having to acquire more capacity.
Creating multiple spans might also help avoid queue split (covered later in this presentation) and help utilize more of the underlying media (IOPS)
Historically, 1 Span per HDP Pool was strongly advocated. This was primarily to avoid a situation where capacity was de-allocated by deleting a file system from 1 span to give to another. In order to unhook the capacity of the deleted file system from the span, requires unmapping. On older HUS class storage, this proved to be an impactful exercise. Modern VSP class storage handles unmap with minimal impact.
More than 1 span, often also results in many file systems, which can result in more I/O load to the back-end. If storage is slow, this could create a bottleneck.

## Slide 34: When not to deploy multiple Spans per HDP Pool
Whenever Unmapping would become a regular occurrence
When a file system is deleted, the HDP pages associated with those chunks are still “mapped” into the Span. They are known as “vacated chunks”.
If a new file system is created within that Span, then the vacated chunks are simply re-used and the mapped capacity is re-used – no un-mapping is performed.
But if the freed up capacity is desired in a different Span, the vacated chunks must be “un-mapped” from that span. The pages are zeroed and returned to the HDP Pool
  This is a slow, background process
  The impact on HUS1x0 storage was significant, but on VSP class storage it has been shown to be far less taxing
  It is also possible to throttle the rate at which un-mapping takes place to avoid creating a large backlog of zeroing activity
Bottom line, is that the unmap process overhead is far less significant on modern storage
Notes: So when should you avoid multiple spans per HDP Pool
Well.. Whenever unmapping would happen regularly… but in truth most implementations rarely use it.
Unmapping has generally not found to be impactful on VSP class storage., although it was a lot more impactful on HUS1x0 storage where it should certainly be avoided.
If you are still concerned about the overhead of unmap, there are CLI commands which can throttle the rate at which HNAS the pages are umapped at the NAS Level, in order to try to pace the back-end and not create a backlog of work.
Finally, consider that just because you can have multiple spans, doesn’t mean you should though.
You should always weigh up the complexity of too many spans and the IO it might create against the back-end configuration. In some cases a single span is just fine.

## Slide 35: Sharing a Span across Nodes – Queue Splits
N1
N2
EVS
SD
SD
SD
SD
SD
FS1
FS2
SP1
If File Systems associated with a Span are mounted on EVS on >1 node, the SD queues will be split by the server accordingly
In a Queue Split scenario, the SDs are shared between Nodes, so SD Queue Depth is divided equally among the Nodes sharing the SDs e.g. Shared 2 ways 32 -> 16
EVS
HDP Pool
Notes: I talked earlier about queue splits – what are those.
Let’s look at a configuration where an HDP Pool has a single span.
On top of that span are two files systems. One FS (FS1) is mounted on one EVS on Node 1 and another FS (FS2) is mounted on an EVS on Node 2.
This means that the System Drives are shared between two nodes (two ways).
The cluster recognizes that the System Drives are shared across two nodes and splits the queue depth of the SDs evenly across the 2 initiators.
Each SD on each node now has a queue depth of 16 rather than 32.
This can lead to reduced performance, especially if the workload is skewed (N1 is heavy/N2 is light)

## Slide 36: Sharing a Span across Nodes – Queue Splits
N1
N2
EVS
SD
SD
SD
SD
SD
FS1
SP1
EVS
SD
SD
SD
SD
SD
FS2
SP2
HDP Pool
If Multiple Spans are created from the same HDP Pool, the Queue Split can be avoided
But you still have to consider the load on the HDP Pool as a whole from >1 span. If the HDP Pool had only a small number of HDDs, creating another Span from it could push it too hard.
Notes: If I create 2 spans, I can avoid the queue split.
Each node gets its own dedicated SDs
Just because I have double the number of SDs though, doesn’t mean I am home free.
If the underlying HDP Pool has limited iops (e.g. 4 PGs of NL-SAS), I could end up over-driving it. In that scenario, it would be best just to keep the 2 EVS on the same node.
So the technique of creating 2 spans on top of the single HDP pool in order to avoid queue splits, may work well in some instances, but not all – it’s easier to oversubscribe the back-end, especially if it’s underpowered.

## Slide 37: Queue Splits are generally discouraged, but..
Queue Split Performance Impact can vary
  More impactful when one node is much busier than the other sharing the system drives
  More impactful with slower disk (NL-SAS), less impactful with SSD/FMD
  The more the queues are split (>2 nodes), the more potential for performance impact
Creating more Spans per HDP pool just to avoid a queue split is not always the best answer
Example: A 4 PG NL-SAS HDP Pool should not be split into 2 spans
  Create a single Span and run the cluster active/passive (if >1 EVS is required, place both on the same node)
  The NL-SAS drives will be the performance bottleneck anyway
Example: A single small PG of Flash should not be split into 2 spans to service only 2 nodes
  Unlikely to reap many benefits by creating 2 spans unless >32 file systems are required
  Simpler just to create a single span and share it across 2 nodes. Increase the Q Depth per SD if required.
Apply some thought.. Keep it simple
Notes: To summarize here.
Splitting the SD queues is generally not a good thing, but how it impacts performance can vary.
The impact is worse in a skewed workload, because it means that one node will be starved, while the other has an overabundance.
The impact is worse when dealing with an underpowered back-end (NL-SAS), its often less impactful with SSD (Flash)
The more you split the queues the worse it is.. E.g. 4 nodes sharing a pool is worse than 2 nodes sharing a pool (4 way split vs 2 way split)
Some instances the solution is straightforward
E.g. Don’t try to split a small NL-SAS HDP Pool into 2 spans to avoid a split. Your bottleneck is going to be the disk back-end, not the node, so simply create 1 pool and try to keep all the EVS on 1 node.
E.g. A single small PG of flash probably is fine as single span with the queue split. As long as you don’t need >32 file systems, this is probably fine.. You can easily bump up the SD queue depth as the back-end can absorb a lot of IO.
So in summary, apply some thought but try to keep it simple.

## Slide 38: 1TB size-limit on allocations on HDP
Span Manager must always know how much free space is on a DP pool, and so it writes to each HDP page in every newly allocated chunk
This takes time, and so
  A new File System on a DP pool can’t exceed 1TiB
  A manual fs-expansion on a DP pool can’t exceed 1TiB
  You can still use multiple expansions to get to 1PiB, or (even better) create a small file system and let it auto-expand
CLI filesystem-expand has the ability to performed looped 1TB expansions, but should be used cautiously
Better to use filesystem-thin and filesystem/span confine if concerned about client perception of capacity. Let auto-expansion do it’s job.
Notes: One of the limitations of HDP Integration, is that the in order to expand (add capacity) to a file system, the system must write a non zero block to each page as it allocates capacity.
This does take some amount of IO and time, therefore file system creation and expansions are limited to 1TB.
This doesn’t mean that you can’t create a 10 or 100TB file system and then let it start at 1TB and auto-expand.. In fact that’s exactly what you should do.
You can combine that with file system thin provisioning that will allow end user/applications to perceive file system capacity as the auto-expansion maximum rather than the fs current size.
There is also a CLI command flag with filesystem-expand –storage-is-lightly-loaded, which allows expansions beyond 1TB, but the process is synchronous and should be done when the system is largely idle

## Slide 39: File System Block Size
HNAS Supports 2 block sizes – 4kb or 32kb
  4kb is more capacity efficient when storing many small files
  32kb provides best performance for most scenarios – especially large block or streaming workloads where throughput is most important
4kb block size tends to place heavier requirement on back-end – more IOPS requires to read/write a given amount of data. Avoid using 4kb on NL-SAS configuration even when storing smaller files.
32kb is and should be the default choice – in most cases it provides the best performance. Most customers say performance isn’t important until it is. If in doubt, use 32kb – especially with NL-SAS drives.
The one exception where 4kb provides better performance is where applications perform small block random write IO into 32kb FS resulting in RMW (Read/Modify/Write)
Notes: The HNAS file system supports two blocks size – 4kb and 32kb
4kb is best suited for capacity efficiency in storing many small files, whereas 32kb is most optimized for IO performance. It is especially beneficial for large block streaming workloads as it requires less ops to read a given amount of data.
4kb tends to place a heavier load on the back-end – more ops requires to read a given amount of data. We recommend against using 4kb file systems on NL-SAS drives.
32kb should be your default choice and the best choice with NL-SAS
One performance exception is when the IO profile is small block in nature. Small block IO writes into a 32kb file system can result in RMW at the FS layer.

## Slide 40: Filesystem level read/modify/write
When a new file is created then the new data is written to new space
When an existing file is extended then the new data is written to new space
However, when an existing file is modified then there are two choices
  write the new data over the top of the existing data (“write in place”)
  write the new data to new space (“write new”)
HNAS normally adopts the “write new” policy
  this is typically more efficient for the backend storage
  this ensures the old data is preserved (when necessary) for features such as snapshots, clones, dedupe, etc.
Notes: Note that this RMW behavior is something specific to the file system layer, this has nothing to do with RMW at the storage/raid layer.
RMW can occur when modifying an existing file. In HNAS we never modify data in pace, we always write out into “free space” or “write new”
HNAS does this so that snapshot blocks are preserved – it allows the file system to easily rollback through pointer manipulation.

## Slide 41: Filesystem level read/modify/write
“Write new” policy writes out new data into free space
New data is written to new space
New data for this position
Old data block is freed (unless required for snapshot etc.)
Updated data for this position
When the data doesn’t cover an entire block, a read is required before updated block can be written
Old data must be read before the block is re-written
Old data block can then be freed (unless required for snapshot etc.)
This read/modify/write can have a dramatic negative impact on performance
This is because it has a huge impact on response time
Notes: It’s easier to understand this with a visual depiction.
Imagine on the left that we have new data that needs to be written (yellow) over the existing cyan. This is pretty straightforward if this is just one block replacing another block.
But looking at the right now… what if the modification is small – it’s a partial block update.
To do that, we have to read the old block in order to merge the partial update with the existing data and then write it out.
This requires us to read the old block, modify it and write it out.
This introduces significant write latency and additional unwanted IO – we have to read from disk, before we can destage and re-write the update.

## Slide 42: Filesystem level read/modify/write
For this reason it is essential to try and avoid the read/modify/write penalty
This can only be done when host/client writes “cover” entire filesystem blocks
This is much more likely with small (4K) blocks than with large (32K) blocks
This is especially true with applications such as VMware which always write in 4K units or Oracle which tends to write in 8k units
Therefore while 32kb is generally the best performing/best choice, one exception is applications that perform small block random writes.
Notes: We therefore try to avoid RMW
It’s more likely to occur when pairing small block random workloads with 32kf file systems.
Oracle OLTP and Vmware are two good examples of small block random workloads that perform poorly on 32kb file system for this reason.
So while 32kb is good for most applications, there are exceptions.

## Slide 43: Implementation Approach

## Slide 44: Size the Pool appropriately
Put some thought into sizing…Avoid the mischaracterization of NAS as a “low I/O workload”.
Even if the front-end load is low, the house keeping tasks (snapshots, replication, deduplication, tiering, etc.. All perform IO)
We do not have an HNAS sizing tool, but you might be able to model using tools like CPK
  SMB/NFS ops DO not equal IOPS
  Write workload is often amplified by file system metadata transactions
  Writes are more expensive than reads
  HNAS attempts to “sequentialize” write IO (Superflush), but Superflush efficiency will degrade over time
  32kb FS are generally more I/O efficient (less IOs required to read/write a given dataset)
Notes:   Let’s talk now about how we implement HDP Thin provisioned storage.
  This must first start with accurate sizing, although in-depth discussion on this topic is beyond the scope of this presentation
  Some things to bear in mind though..
  SMB/NFS ops DO not equal IOPS – sometimes 1 NFS/SMB op = multiple disk ops, sometimes the opposite is true.
  HNAS does have a dedicated metadata read cache, but it can be overwhelmed during certain workloads forcing more small block random read workload
  Write workload is often amplified i.e. 1 SMB/NFS write, will often require multiple IO writes. Nature of a file system that writes out redundant metadata structures + the data itself. Other phenomena can result in further amplification.. Plan for the fact that it will happen.
  As a result a 70/30 front end mix, might end up being 60/40 to the back end. Writes are more expensive than reads.
  HNAS does attempt to “sequentialize” write IO (Superflush). This works well on a fresh file system, but over time the amount of superflush will decrease. Therefore plan for writes to become more random over time. Superflush block size is 384kb, but non-superflush write IOs vary between 4kb and 32kb. File system block size influences read/write IO size, but metadata operations are often smaller IOs

## Slide 45: General Recommendations
Use THIN PROVISIONED Spans – 2-3X is strongly encouraged
One Span per HDP pool, although Multiple Spans per HDP Pool should be considered in many cases.
Tiered File System almost always require two (separate) HDP Pools, but can use HDT (pinning)
Avoid sharing an HDP pool between two or more clusters
Sharing a pool between HNAS and foreign servers is supported but not recommended. HNAS is thin friendly, foreign servers are often not
Avoid Splitting Queues, but be pragmatic
But… many of these rules aren’t set in stone and should be adapted to configuration and circumstances
Notes: In terms of a set of high level recommendation.
First and foremost – leverage thin provisioning – 200-300% over provisioning is recommended.
One span per HDP pool is the base recommendation, but multiple spans per HDP pool can be deployed depending on the situation at hand
If you decided to implement TFS, then we would recommend two separate HDP pools to separate the different storage types, although it could be implemented as a single HDT Pool and the Tier 0 Metadata DP Volumes could be pinned into Flash (Tier 1) media.
An HDP Pool should be dedicated to a NAS Cluster. It should not be shared with other clusters or with other block hosts.
Why not? First off. HNAS is thin friendly – it is designed to work with thin provisioned pools. Other block hosts operating systems may not be thin friendly and therefore may not operate reliably with a thin provisioned pool.
More often than not though the reason to keep the HDP Pool dedicated is to provide predictable performance. NAS clusters have a habit of creating quite intensive workloads that could interfere with other cluster or other hosts sharing that pool and vice versa.
As mentioned previously queue splits should be avoided.
But many of these practices are guideines and should be adapted according to the workload and configuration. Every circumstances if unique.

## Slide 46: Creating the DP Volumes for the Span
How many and what size?
Don’t get too caught up in the minutiae
For HDDs based pools
  1 or 2 DP Volumes per PG (8 HDDs)
  Size of the volumes should be based on the oversubscription ratio vs physical capacity
You must queue IO to drive the storage
  Too much queued IO increases storage latency, which can hurt performance
  Too little queued IO decreases storage latency but can increase client latency / reduce ops
  Default per SD queue depth is 32, but can be changed dynamically through the CLI
  Sd-set -q
Notes: When creating the DP Pool and DP Volumes for NAS to consume, customers often struggle to understand how many volumes should be created and what size they should be.
There’s some general guidance that can be provided here, but the guidance here is just that.. Don’t try to get too caught up in the minutiae and try to make it into an exact science, because it isn’t
General speaking for HDD based pools, create 1-2 DP Volumes per 6+2 PG. Certainly 2 DP Volumes for each 14+2 PG.
The size of the volumes should be based on the oversubscription ratio. E.g. If you have 100TB across 4 PGs of 7+1 R5 HDDs, then 4 DP Volumes @50TB each = 200TB – that is an oversubscription of 200%. Equally 8 DP Volumes at 25TB would probably be fine, since that would also be 200% over subscription.
The number of SD is a balance of a few things..
You need at least 4 SDs to form a span. More SD creates more a bit more parallelism, but too much can overwhelm the back-end drives. Each SD by default will queue 32 IOs (default QD). Too few queue IOs means that you don’t drive the back-end hard enough, the application latency might go up, because it’s not pushing the back-end. Too many queue IOs means that you overdrive the back-end and the latency of the storage will go up, which can also negatively impact performance.
The good news is that per SD queue depth can be dynamically changed via the CLI. So if you initially create 4 SDs, but want to increase QD, you can do that via the CLI.
Let’s look at a few examples:

## Slide 47: Quick Example 1
100TB of capacity on a VSP400 Unified
  100TB of 2.4TB 10k drives = 64 drives or 8 PGs @6+2 R6
  Customer estimates minimal growth, but not sure what will grow
  Customer has requirement for Multi-Tenancy (a few small EVS), only 1 EVS is likely to have a heavier IO load
  Most of the workload is general user shares and some image repositories for apps.
Considerations
  Creating 2 Spans on the HDP Pool would provide Active EVS on each of the 2 nodes without splitting queues
  Both Spans can get capacity from a single HDP pool, but the 1 busy EVS has full access to all 64 HDDs for performance
  Minimal growth so 2:1 oversubscription should be sufficient (2 x 100TB Spans)
Notes: Let’s consider a VSP400 Unified.
100TB of 2.4TB 10k drives = 64 drives or 8 PGs
Customer doesn’t believe his configuration will grow much but isn’t sure.
Customer has a requirement for multiple EVS, only 1 EVS is likely to have a heavier load.
In this case, we could
Create 1 Span with 8 or 16 SDs that provides 200TB total or 2 Spans with 100TB each.
A single span would result in queue split if the EVS run on both nodes
Two spans could be placed across a single HDP Pool.. So even if 1 EVS on N1 pushed hard, it could use all the underlying PGs without a queue split

## Slide 48: Quick Example 1: Solution
Single HDP Pool with 16 DP Volumes @12.5TB (200TB THIN)
  Span 1 – 8 SD@12.5TB
  Span 2 – 8 SD@12.5TB
If we find Span 1 hosts the more demanding EVS, we could consider raising the Q Depth on the SDs
As we add more PGs (for capacity), we could also consider raising the Q Depth on the SDs
Use 32kb FS block size for the file systems
Notes: Let’s assume we did use 2 Spans then
Single HDP Pool with 16 DP Volumes @12.5TB
8 for Span 1, 8 for Span 2
As we add more PGs over time, we could raise the QD

## Slide 49: Quick Example 2
400TB capacity requirement
  Not a requirement for multi-tenancy but needs high read performance (up to 14 GB/sec read)
  Offload older data to Cloud, active data growth expected to be minimal, but not predictable
Account team settles on 4 node HNAS5300 using E990 w/400TB NVME/SSD
  10 x 6+2R6 7.6TB NVME/SSD
Considerations
  Single EVS per node required to harness all 4 nodes, may includes namespace/read cache
  Carving up the SSDs into a single Span per node on a single HDP pool will provide some flexibility on how capacity can be allocated.
Notes: Let’s look at another example
In this example, we have a 400TB Capacity requirement. There’s not a mutli-tenancy requirement here, but there is an emphasis on performance and reaching up to 14GB/sec (READ)
The customer expect to offload older / in active data to cloud, so growth is expected to be minimal.
The account team settles on a 4 node 5300 using an E990 w/400TB – 10 x 6+2R6 7.6TB SSD

## Slide 50: Quick Example 2: Solution
Oversubscribe @2:1, but need adequate volumes to drive the SSD, but also provide capacity where needed.
16 volumes across 4 Spans = 64 DP Volumes
400 x 2 = 800 DP Pool / 64 Volumes = 12.5TB Volumes
  4 Spans 16 SDs x 12.5TB Volumes with 1 EVS per node
32kb File System to provide best throughput
  CNS/CRC might enhance throughput for NFSv3 read intensive operations of individual files
4 Nodes provides a max. of 18GB/sec but can still provide 13.5GB/sec if a node fails

## Slide 51: UVM

## Slide 52: Universal Volume Manager and Hitachi NAS
UVM (Virtualization) is supported with Hitachi NAS, but is generally not considered to be a high performance solution
UVM Storage can be utilized in two ways:
Pass-through
  External LUNs are presented by other storage systems; the local array virtualizes the external LUNs and presents them to the server as internal LUNs
HDP
  External LUNs are presented by other storage systems; the local array virtualizes the external LUNs and uses them as HDP Pool Volumes. The local array presents DP Volumes to the HNAS from this HDP Pool.
Notes: UVM (Universal Volume Manager) is supported with Hitachi NAS, but is generally not a good high performance solution owing to the need to re-issue the IO through the VSP controlller to the external array.
There’s essentially two ways in which UVM could be deployed.
In a pass through or via HDP
Pass-through is typically used when an existing HDP Pool is used with HNAS, but there’s a desire to virtualize it behind a VSP array. The existing LUN configuration is basically re-presented through the VSP.
HDP is typically used with a new deployment e.g. if there’s a requirement to utilize a 3rd party array with HNAS or the customer has some additional capacity that he’d like to redeploy through an existing VSP

## Slide 53: Pass-through
With UVM pass-through, the server has no way to determine whether the external LUs are thinly provisioned (even if they come from an HDP Pool on the external array).
It therefore does not know how much free disk space is left
The HNAS server is therefore unable to guard against running out of disk space as effectively as it can with a local HDP pool.
It is therefore the administrator's job to ensure that no external HDP pool ever runs out of space.
Notes: Pass-through presents some challenges to HNAS, since even if the external Hitachi array with an HDP Pool, the HNAS can no longer directly interrogate the HDP Pool. Therefore even if the Pool were thin provisioned, the HNAS would no longer understand the real capacity. It therefore becomes the Administrator’s responsibility to maintain free space.
To migrate a pool to a UVM pool.
Dismount the file systems.
Re-present the LUNs to the HNAS via UVM
Use 'sd-allow-access' to license the 'new' SDs.
Wait for Cod to load by running 'span-wait-for-loading'. The server will log events about changed Luids.
If 'span-list' shows the failed span, unload it by typing 'sd-rescan-cod <span-instance-name>'.
Use 'span-wait-for-loading' to wait for Cod to be rescanned
Use 'sd-list-changed-luids' to check that the server has detected all changed Luids.
Use 'sd-recover-from-changed-luids' to make the server reload spans.
Run 'span-wait-for-loading' to wait for the Cod to load. Run 'span-list' to see which spans have been recovered.
Use 'span-rewrite-cod' to update the Cod, reflecting the updated configuration.
Mount file systems.
Use 'sd-forget' to remove the 'old' SDs from the server's registry.

## Slide 54: UVM Pass-through - Differences
When working with UVM based storage, the server will treat the storage a bit differently:
  Span-list will show UVM in place of “Con”. Will not show HDP free space.
  Auto-expansion is disabled. Administrator responsible for ensuring capacity is available
  Vacated chunks list is still maintained, but you cannot unmap (span-unmap-vacated-chunks is not available)
It is possible to migrate a UVM based pool to a local HDP Pool using HTSM
  Be aware that the target pool will be THICK
Notes: UVM based storage that is used in pass through has some limitations – mostly due to the fact that the server can no longer detect the nature of HDP and the available free space
Since it can no longer interrogate the HDP Layer, it won’t show the available free space, nor will it allow auto-expansion of the span
While the server still performs pre-allocation, and a vacated chunks list, you can no longer use unmap
It is possible to use HSTM to migrate a UVM based pool to local HDP pool, but be aware that doing so will result in the pool becoming THICK
E.g. if the existing HDP Pool that is being virtualized has 8 x 10TB Volumes based on 40TB of Pool Volumes, if HTSM is used to migrate to another HDP pool. That HDP Pool will require 80TB of capacity.

## Slide 55: UVM HDP Pool
If you elect to build a local HDP Pool based on Pool Volumes from an external array, the Hitachi NAS treats the storage as a local HDP Pool,
  Span-list shows HDP available capacity
  Auto-expansion is available
  Unmap (span-unmap-vacated-chunks) is still available
HTSM could still be used to migrate external pool volumes to internal pool volumes
  The HDP pool would remain THIN
Notes: If you elect to use external storage with HNAS, and you’re not forced into re-using an existing span, then the best way it to create the HDP pool locally, but utilize external pool volumes.
In this fashion, the HNAS continues to operate with the HDP pool in a local manner – it will be able to understand real free capacity, auto-expansion will still be available, as will unamp
If HTSM is used to migrate the external array to internal volumes, the HDP pool would remain THIN, since this would simply be copying the thick pool volumes, the DP Volumes would stay the same.

## Slide 56: ADR

## Slide 57: HDP Thin Provisioning
Thin Provisioned HDP Pools has been a “best practice” since release 12.1.
HNAS spans are typically deployed on overprovisioned HDP Pools
This mechanism allows customers to easily scale NAS capacity incrementally with zero disruption and automatic load-levelling.
HNAS uses SCSI commands to obtain available physical free space from the storage system to avoid prematurely exhausting physical capacity
A similar inband approach is used with Hitachi Accelerated Flash module drives (FMDs) when deployed on VSP Unified Platform
ADR does not provide HNAS with a similar in band SCSI interface to allow it to query physical capacity

## Slide 58: SVOS RF ADR and Hitachi NAS
SVOS RF based data reduction does not currently report in-band data reduction level or physical pool utilization
As such an HNAS system cannot accurately measure the physical free space available to HNAS file systems
  This is in stark contrast to the typical thin provisioned pool deployment
Since the HNAS is unable to measure physical free space in this configuration, it cannot prevent a catastrophic capacity exhaustion event
  Should that occur, all file systems of the host pool would be forced offline until more capacity is added to the pool
While ADR is supported with HNAS, it is not recommended for these reasons
Customers who choose to deploy it must vigilantly manage free space at the storage subsystem level (since the HNAS is not provided the capability to do so)
Notes: Contrary to Hitachi Accelerated Flash module drives (FMDs) physical capacity statistics reporting with Hitachi VSP Unified or VSP N, SVOS RF-based data reduction does not currently report in-band the data reduction levels or physical pool utilization level of the host HDP Pool. As such a HNAS system attached to an HDP Pool that is leveraging SVOS RF ADR cannot accurately measure the physical free space available to the HNAS file systems
Since the HNAS in unable to measure actual physical free space when ADR is deployed, it cannot prevent a catastrophic capacity exhaustion event – an attempt made by the system to write to a mounted file system that fails due to lack of available free space (that was previously provided by HDP Integration). In such an event, the file system and its host span will fail and remain offline until additional capacity can be acquired and provisioned to the underlying pool. If this is the only HDP pool used by the NAS system, all NAS resource would be rendered offline, until the situation is rectified (by acquisition of additional capacity).
While the use of SVOS RF ADR with HDP Pools attached to HNAS is a supported configuration, for these reasons it is not recommended.
Customers who choose to leverage SVOS RF ADR with HDP Pools used by HNAS, must acknowledge and understand that free space management must be performed by consulting the storage system itself for free space information

## Slide 59: Hitachi NAS De-Duplication
Hitachi NAS provides its own HW Assisted De-Duplication
The FPGA Accelerated De-Duplication within HNAS is a post process implementation
  The system regularly reclaims redundant blocks within file system that are formatted with deduplication support
  The rate at which data is processed can be increased by licensing premium deduplication (200MB/sec -> 550MB/sec)
The Hitachi NAS System file system is fully integrated into the deduplication engine
  The capacity savings are instantly realized and are fully visible to end user/applications
Minimal performance impact
  While deduplication is a post process implementation, the “heavy lifting” of hash generation is offload to the FPGA engine to limit performance impact.
  DeDupe essentially runs as required, although it can be configured to operate within windows

## Slide 60: Thank You